## Instrucciones
Welcome to PywerAPM | Module Circuit Breaker

## CB_SF6
Company | Asset_Type | ID | Serial | Location | Opt_Year | U_Nom | Brand | Model | Type | Replacement | Load | UC
WAKANDA_TSO | CB_SF6 | CB_03 | 13 | BOG_3 | 2006 | 230 | ABB | LTB 245E1 | Transformer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_04 | 14 | BOG_4 | 2006 | 500 | AREVA | GL317 | Transformer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_07 | 15 | BOG_7 | 2010 | 230 | AREVA | GL-314 F3_1 | Transformer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_08 | 16 | BOG_8 | 1997 | 230 | ABB | HGA 300/4002-B | Transformer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_12 | 17 | BOG_12 | 2015 | 500 | ALSTOM | GL317 | Transformer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_15 | 18 | BOG_15 | 2006 | 500 | AREVA | GL317 | Transformer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_16 | 19 | BOG_16 | 2010 | 230 | AREVA | GL-314 F3_1 | Transformer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_18 | 20 | BOG_18 | 1997 | 230 | ASEA | HLR 245/2502E2 | Transformer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_20 | 21 | BOG_20 | 1997 | 230 | ASEA | HGA 300/4002X | Transformer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_21 | 22 | BOG_21 | 2007 | 230 | CROMPTON GREAVE | 200-SFM-40S_1 | Transformer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_23 | 23 | BOG_23 | 1997 | 230 | ASEA | HLR 245/2502E2 | Transformer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_24 | 24 | BOG_24 | 1997 | 230 | ASEA | HGA 300/4002X | Transformer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_25 | 25 | BOG_25 | 2007 | 230 | CROMPTON GREAVE | 200-SFM-40S_1 | Transformer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_26 | 26 | BOG_26 | 2006 | 230 | CROMPTON GREAVE | 200-SFM-40S | Transformer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_27 | 27 | BOG_27 | 1997 | 230 | MITSUBISHI | 200-SFM-40A-2 | Transformer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_28 | 28 | BOG_28 | 1997 | 115 | MITSUBISHI | 100-SFM-32B -2 | Transformer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_29 | 29 | BOG_29 | 1997 | 115 | OERLIKON | TOFQ-150.12 | Transfer | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_31 | 30 | BOG_31 | 2016 | 115 | SIEMENS | 3AP1_A | Line | False | None | N5S2
WAKANDA_TSO | CB_SF6 | CB_39 | 31 | BOG_39 | 1997 | 115 | SPRECHER+SCHUH | HPF 311 LS-A | Line | False | None | N5S2
Note on I2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Se cambio BLG 1002A por LTB 245E1, preguntar si es valido.
Note on J1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Transformer OHL Switch Transfer
Note on K1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Si tiene respuesto

## Resistance
Test_ID | Pos | Serial | Location | Date | R_Contact | R_Dynamic
1 | CB_03 | 13 | BOG | 2015-04-22 | 0 | 1
2 | CB_03 | 13 | BOG | 2015-06-17 | 1 | 2
4 | CB_03 | 13 | BOG | 2015-12-12 | 2 | 1
5 | CB_03 | 13 | BOG | 2017-07-13 | 1 | 1
6 | CB_03 | 13 | BOG | 2018-06-21 | 2 | 2
7 | CB_03 | 13 | BOG | 2019-03-18 | 2 | 2
8 | CB_04 | 14 | BOG | 2012-02-17 | 2 | 2
9 | CB_04 | 14 | BOG | 2013-09-06 | 2 | 2
10 | CB_04 | 14 | BOG | 2014-05-26 | 3 | 2
11 | CB_04 | 14 | BOG | 2015-06-18 | 2 | 2
12 | CB_04 | 14 | BOG | 2017-07-17 | 3 | 2
13 | CB_04 | 14 | BOG | 2019-01-11 | 4 | 2
14 | CB_07 | 15 | BOG | 2011-08-26 | 0 | 1
15 | CB_07 | 15 | BOG | 2013-09-25 | 0 | 1
16 | CB_07 | 15 | BOG | 2014-07-18 | 1 | 1
17 | CB_07 | 15 | BOG | 2015-04-22 | 1 | 1
18 | CB_07 | 15 | BOG | 2017-06-27 | 2 | 1
19 | CB_07 | 15 | BOG | 2019-01-11 | 3 | 1
20 | CB_07 | 15 | BOG | 2019-02-20 | 4 | 2
21 | CB_08 | 16 | BOG | 2015-04-22 | 0 | 1
22 | CB_08 | 16 | BOG | 2015-06-17 | 0 | 2
24 | CB_08 | 16 | BOG | 2015-12-12 | 1 | 2
25 | CB_08 | 16 | BOG | 2017-07-13 | 1 | 2
26 | CB_08 | 16 | BOG | 2018-06-21 | 2 | 2
27 | CB_08 | 16 | BOG | 2019-03-18 | 0 | 2
28 | CB_12 | 17 | BOG | 2012-02-17 | 1 | 1
29 | CB_12 | 17 | BOG | 2013-09-06 | 2 | 1
30 | CB_12 | 17 | BOG | 2014-05-26 | 2 | 1
31 | CB_12 | 17 | BOG | 2015-06-18 | 2 | 1
32 | CB_12 | 17 | BOG | 2017-07-17 | 2 | 1
33 | CB_12 | 17 | BOG | 2019-01-11 | 2 | 1
34 | CB_15 | 18 | BOG | 2011-08-26 | 0 | 1
35 | CB_15 | 18 | BOG | 2013-09-25 | 0 | 1
36 | CB_15 | 18 | BOG | 2014-07-18 | 1 | 1
37 | CB_15 | 18 | BOG | 2015-04-22 | 1 | 1
38 | CB_15 | 18 | BOG | 2017-06-27 | 1 | 1
39 | CB_15 | 18 | BOG | 2019-01-11 | 1 | 1
40 | CB_15 | 18 | BOG | 2019-02-20 | 1 | 1
41 | CB_16 | 19 | BOG | 2015-04-22 | 0 | 2
42 | CB_16 | 19 | BOG | 2015-06-17 | 2 | 2
44 | CB_16 | 19 | BOG | 2015-12-12 | 2 | 2
45 | CB_16 | 19 | BOG | 2017-07-13 | 2 | 2
46 | CB_16 | 19 | BOG | 2018-06-21 | 2 | 2
47 | CB_16 | 19 | BOG | 2019-03-18 | 2 | 2
48 | CB_18 | 20 | BOG | 2012-02-17 | 1 | 1
49 | CB_18 | 20 | BOG | 2013-09-06 | 3 | 1
50 | CB_18 | 20 | BOG | 2014-05-26 | 3 | 1
51 | CB_18 | 20 | BOG | 2015-06-18 | 3 | 1
52 | CB_18 | 20 | BOG | 2017-07-17 | 3 | 1
53 | CB_18 | 20 | BOG | 2019-01-11 | 3 | 1
54 | CB_20 | 21 | BOG | 2011-08-26 | 1 | 1
55 | CB_20 | 21 | BOG | 2013-09-25 | 0 | 1
56 | CB_20 | 21 | BOG | 2014-07-18 | 0 | 1
57 | CB_20 | 21 | BOG | 2015-04-22 | 1 | 1
58 | CB_20 | 21 | BOG | 2017-06-27 | 1 | 1
59 | CB_20 | 21 | BOG | 2019-01-11 | 1 | 1
60 | CB_20 | 21 | BOG | 2019-02-20 | 1 | 1
61 | CB_21 | 22 | BOG | 2011-08-26 | 2 | 1
62 | CB_21 | 22 | BOG | 2013-09-25 | 1 | 2
63 | CB_21 | 22 | BOG | 2014-07-18 | 2 | 2
64 | CB_21 | 22 | BOG | 2015-04-22 | 2 | 2
65 | CB_21 | 22 | BOG | 2017-06-27 | 2 | 2
66 | CB_21 | 22 | BOG | 2019-01-11 | 2 | 2
67 | CB_21 | 22 | BOG | 2019-02-20 | 2 | 2
68 | CB_23 | 23 | BOG | 2015-04-22 | 0 | 2
69 | CB_23 | 23 | BOG | 2015-06-17 | 3 | 2
71 | CB_23 | 23 | BOG | 2015-12-12 | 3 | 2
72 | CB_23 | 23 | BOG | 2017-07-13 | 3 | 2
73 | CB_23 | 23 | BOG | 2018-06-21 | 3 | 2
74 | CB_23 | 23 | BOG | 2019-03-18 | 4 | 2
75 | CB_24 | 24 | BOG | 2012-02-17 | 2 | 1
76 | CB_24 | 24 | BOG | 2013-09-06 | 2 | 1
77 | CB_24 | 24 | BOG | 2014-05-26 | 2 | 2
78 | CB_24 | 24 | BOG | 2015-06-18 | 2 | 2
79 | CB_24 | 24 | BOG | 2017-07-17 | 2 | 2
80 | CB_24 | 24 | BOG | 2019-01-11 | 2 | 2
81 | CB_25 | 25 | BOG | 2011-08-26 | 0 | 1
82 | CB_25 | 25 | BOG | 2013-09-25 | 0 | 1
83 | CB_25 | 25 | BOG | 2014-07-18 | 1 | 1
84 | CB_25 | 25 | BOG | 2015-04-22 | 1 | 1
85 | CB_25 | 25 | BOG | 2017-06-27 | 1 | 2
86 | CB_25 | 25 | BOG | 2019-01-11 | 1 | 3
87 | CB_25 | 25 | BOG | 2019-02-20 | 2 | 4
88 | CB_26 | 26 | BOG | 2015-04-22 | 1 | 1
89 | CB_26 | 26 | BOG | 2015-06-17 | 0 | 1
91 | CB_26 | 26 | BOG | 2015-12-12 | 1 | 1
92 | CB_26 | 26 | BOG | 2017-07-13 | 1 | 1
93 | CB_26 | 26 | BOG | 2018-06-21 | 2 | 3
94 | CB_26 | 26 | BOG | 2019-03-18 | 3 | 4
95 | CB_27 | 27 | BOG | 2012-02-17 | 0 | 1
96 | CB_27 | 27 | BOG | 2013-09-06 | 0 | 1
97 | CB_27 | 27 | BOG | 2014-05-26 | 1 | 1
98 | CB_27 | 27 | BOG | 2015-06-18 | 1 | 1
99 | CB_27 | 27 | BOG | 2017-07-17 | 1 | 1
100 | CB_27 | 27 | BOG | 2019-01-11 | 1 | 1
101 | CB_28 | 28 | BOG | 2011-08-26 | 1 | 1
102 | CB_28 | 28 | BOG | 2013-09-25 | 1 | 1
103 | CB_28 | 28 | BOG | 2014-07-18 | 1 | 1
104 | CB_28 | 28 | BOG | 2015-04-22 | 1 | 1
105 | CB_28 | 28 | BOG | 2017-06-27 | 1 | 1
106 | CB_28 | 28 | BOG | 2019-01-11 | 1 | 1
107 | CB_28 | 28 | BOG | 2019-02-20 | 2 | 1
108 | CB_29 | 29 | BOG | 2011-08-26 | 2 | 1
109 | CB_29 | 29 | BOG | 2013-09-25 | 2 | 1
110 | CB_29 | 29 | BOG | 2014-07-18 | 2 | 1
111 | CB_29 | 29 | BOG | 2015-04-22 | 2 | 1
112 | CB_29 | 29 | BOG | 2017-06-27 | 2 | 1
113 | CB_29 | 29 | BOG | 2019-01-11 | 2 | 1
114 | CB_29 | 29 | BOG | 2019-02-20 | 2 | 1
115 | CB_31 | 30 | BOG | 2015-04-22 | 0 | 2
116 | CB_31 | 30 | BOG | 2015-06-17 | 1 | 2
117 | CB_31 | 30 | BOG | 2015-12-12 | 1 | 2
118 | CB_31 | 30 | BOG | 2017-07-13 | 1 | 2
119 | CB_31 | 30 | BOG | 2018-06-21 | 1 | 2
120 | CB_31 | 30 | BOG | 2019-03-18 | 1 | 2
121 | CB_39 | 31 | BOG | 2012-02-17 | 0 | 2
122 | CB_39 | 31 | BOG | 2013-09-06 | 1 | 2
123 | CB_39 | 31 | BOG | 2014-05-26 | 1 | 2
124 | CB_39 | 31 | BOG | 2015-06-18 | 1 | 2
125 | CB_39 | 31 | BOG | 2017-07-17 | 2 | 2
126 | CB_39 | 31 | BOG | 2019-01-11 | 2 | 3

## GAS
Test_ID | Pos | Serial | Location | Date | SF6_Leaks | Gas_Condition | Purity | Presure | Opt | Humidity | Acidity
1 | CB_03 | 13 | BOG | 2015-04-22 | 0 | 0
2 | CB_03 | 13 | BOG | 2017-07-13 | 0 | 0
3 | CB_03 | 13 | BOG | 2018-06-21 | 0.1 | 0
4 | CB_03 | 13 | BOG | 2019-03-18 | 0.1 | 1
5 | CB_04 | 14 | BOG | 2012-02-17 | 0 | 2
6 | CB_04 | 14 | BOG | 2013-09-06 | 0.5 | 2
7 | CB_04 | 14 | BOG | 2014-05-26 | 1 | 2
8 | CB_04 | 14 | BOG | 2017-07-17 | 1.5 | 3
9 | CB_04 | 14 | BOG | 2019-01-11 | 2.1 | 3
10 | CB_07 | 15 | BOG | 2011-08-26 | 0.5 | 1
11 | CB_07 | 15 | BOG | 2014-07-18 | 0.6 | 1
12 | CB_07 | 15 | BOG | 2015-04-22 | 0.7 | 1
13 | CB_07 | 15 | BOG | 2017-06-27 | 0.7 | 1
14 | CB_07 | 15 | BOG | 2019-01-11 | 0.8 | 1
15 | CB_07 | 15 | BOG | 2019-02-20 | 0.8 | 1
16 | CB_08 | 16 | BOG | 2015-04-22 | 1 | 1
17 | CB_08 | 16 | BOG | 2015-12-12 | 1.2 | 2
18 | CB_08 | 16 | BOG | 2018-06-21 | 1.3 | 2
19 | CB_08 | 16 | BOG | 2019-03-18 | 1.5 | 2
20 | CB_12 | 17 | BOG | 2012-02-17 | 1.1 | 0
21 | CB_12 | 17 | BOG | 2014-05-26 | 1.2 | 0
22 | CB_12 | 17 | BOG | 2015-06-18 | 1.4 | 0
23 | CB_12 | 17 | BOG | 2019-01-11 | 1.8 | 1
24 | CB_15 | 18 | BOG | 2011-08-26 | 0.2 | 1
25 | CB_15 | 18 | BOG | 2013-09-25 | 0.7 | 2
26 | CB_15 | 18 | BOG | 2014-07-18 | 0.7 | 2
27 | CB_15 | 18 | BOG | 2017-06-27 | 0.8 | 2
28 | CB_15 | 18 | BOG | 2019-01-11 | 0.8 | 2
29 | CB_15 | 18 | BOG | 2019-02-20 | 0.9 | 3
30 | CB_16 | 19 | BOG | 2015-06-17 | 1.1 | 1
31 | CB_16 | 19 | BOG | 2015-12-12 | 1.2 | 1
32 | CB_16 | 19 | BOG | 2017-07-13 | 1.3 | 1
33 | CB_16 | 19 | BOG | 2018-06-21 | 1.3 | 1
34 | CB_16 | 19 | BOG | 2019-03-18 | 1.4 | 1
35 | CB_18 | 20 | BOG | 2013-09-06 | 0.5 | 2
36 | CB_18 | 20 | BOG | 2014-05-26 | 0.5 | 2
37 | CB_18 | 20 | BOG | 2015-06-18 | 0.5 | 2
38 | CB_18 | 20 | BOG | 2019-01-11 | 0.6 | 2
39 | CB_20 | 21 | BOG | 2011-08-26 | 0.3 | 1
40 | CB_20 | 21 | BOG | 2013-09-25 | 0.3 | 1
41 | CB_20 | 21 | BOG | 2014-07-18 | 0.4 | 1
42 | CB_20 | 21 | BOG | 2017-06-27 | 0.4 | 1
43 | CB_20 | 21 | BOG | 2019-01-11 | 0.6 | 1
44 | CB_20 | 21 | BOG | 2019-02-20 | 0.7 | 1
45 | CB_21 | 22 | BOG | 2011-08-26 | 0.4 | 0
46 | CB_21 | 22 | BOG | 2014-07-18 | 0.4 | 0
47 | CB_21 | 22 | BOG | 2015-04-22 | 0.4 | 0
48 | CB_21 | 22 | BOG | 2017-06-27 | 0.6 | 0
49 | CB_21 | 22 | BOG | 2019-02-20 | 0.6 | 1
50 | CB_23 | 23 | BOG | 2015-04-22 | 0.7 | 2
51 | CB_23 | 23 | BOG | 2015-12-12 | 1.1 | 2
52 | CB_23 | 23 | BOG | 2017-07-13 | 1.1 | 2
53 | CB_23 | 23 | BOG | 2019-03-18 | 2 | 2
54 | CB_24 | 24 | BOG | 2012-02-17 | 1 | 1
55 | CB_24 | 24 | BOG | 2015-06-18 | 1 | 2
56 | CB_24 | 24 | BOG | 2017-07-17 | 1 | 2
57 | CB_24 | 24 | BOG | 2019-01-11 | 1 | 2
58 | CB_25 | 25 | BOG | 2011-08-26 | 0.5 | 0
59 | CB_25 | 25 | BOG | 2014-07-18 | 0.5 | 0
60 | CB_25 | 25 | BOG | 2017-06-27 | 0.5 | 0
61 | CB_25 | 25 | BOG | 2019-01-11 | 0.5 | 0
62 | CB_25 | 25 | BOG | 2019-02-20 | 0.5 | 0
63 | CB_26 | 26 | BOG | 2015-04-22 | 1.2 | 1
64 | CB_26 | 26 | BOG | 2015-06-17 | 1.5 | 2
65 | CB_26 | 26 | BOG | 2015-12-12 | 1.8 | 2
66 | CB_26 | 26 | BOG | 2018-06-21 | 1.9 | 1
67 | CB_26 | 26 | BOG | 2019-03-18 | 2 | 2
68 | CB_27 | 27 | BOG | 2012-02-17 | 0.6 | 0
69 | CB_27 | 27 | BOG | 2013-09-06 | 0.7 | 0
70 | CB_27 | 27 | BOG | 2014-05-26 | 0.7 | 0
71 | CB_27 | 27 | BOG | 2015-06-18 | 0.8 | 0
72 | CB_27 | 27 | BOG | 2017-07-17 | 0.8 | 0
73 | CB_27 | 27 | BOG | 2019-01-11 | 0.8 | 0
74 | CB_28 | 28 | BOG | 2011-08-26 | 1.2 | 1
75 | CB_28 | 28 | BOG | 2013-09-25 | 1.3 | 1
76 | CB_28 | 28 | BOG | 2014-07-18 | 1.4 | 1
77 | CB_28 | 28 | BOG | 2017-06-27 | 1.4 | 1
78 | CB_28 | 28 | BOG | 2019-01-11 | 1.4 | 1
79 | CB_28 | 28 | BOG | 2019-02-20 | 1.5 | 1
80 | CB_29 | 29 | BOG | 2011-08-26 | 1.1 | 1
81 | CB_29 | 29 | BOG | 2013-09-25 | 1.2 | 2
82 | CB_29 | 29 | BOG | 2014-07-18 | 1 | 2
83 | CB_29 | 29 | BOG | 2017-06-27 | 1.4 | 2
84 | CB_29 | 29 | BOG | 2019-01-11 | 1.5 | 2
85 | CB_29 | 29 | BOG | 2019-02-20 | 1.5 | 2
86 | CB_31 | 30 | BOG | 2015-04-22 | 0.6 | 0
87 | CB_31 | 30 | BOG | 2015-06-17 | 0.7 | 0
88 | CB_31 | 30 | BOG | 2015-12-12 | 0.8 | 0
89 | CB_31 | 30 | BOG | 2017-07-13 | 0.9 | 0
90 | CB_31 | 30 | BOG | 2018-06-21 | 1 | 0
91 | CB_31 | 30 | BOG | 2019-03-18 | 1.1 | 0
92 | CB_39 | 31 | BOG | 2013-09-06 | 0.7 | 1
93 | CB_39 | 31 | BOG | 2014-05-26 | 0.8 | 1
94 | CB_39 | 31 | BOG | 2015-06-18 | 0.2 | 1
95 | CB_39 | 31 | BOG | 2017-07-17 | 0.1 | 1
96 | CB_39 | 31 | BOG | 2019-01-11 | 0.3 | 1

## Mechanism
Test_ID | Pos | Serial | Location | Date | Recharge_Time | Tank | Bushings
1 | CB_03 | 13 | BOG | 2015-04-22 | 1 | 0 | 1
2 | CB_03 | 13 | BOG | 2017-07-13 | 1 | 2 | 2
3 | CB_03 | 13 | BOG | 2019-03-18 | 1 | 2 | 2
4 | CB_04 | 14 | BOG | 2013-09-06 | 0 | 1 | 1
5 | CB_04 | 14 | BOG | 2017-07-17 | 0 | 1 | 1
6 | CB_04 | 14 | BOG | 2019-01-11 | 0 | 2 | 1
7 | CB_07 | 15 | BOG | 2011-08-26 | 1 | 0 | 2
8 | CB_07 | 15 | BOG | 2014-07-18 | 2 | 0 | 2
9 | CB_07 | 15 | BOG | 2017-06-27 | 3 | 0 | 2
10 | CB_07 | 15 | BOG | 2019-01-11 | 3 | 0 | 2
11 | CB_08 | 16 | BOG | 2015-04-22 | 1 | 1 | 1
12 | CB_12 | 17 | BOG | 2012-02-17 | 1 | 0 | 0
13 | CB_12 | 17 | BOG | 2014-05-26 | 1 | 0 | 0
14 | CB_12 | 17 | BOG | 2019-01-11 | 2 | 0 | 0
15 | CB_15 | 18 | BOG | 2011-08-26 | 0 | 1 | 1
16 | CB_15 | 18 | BOG | 2014-07-18 | 0 | 1 | 1
17 | CB_15 | 18 | BOG | 2019-01-11 | 0 | 1 | 1
18 | CB_15 | 18 | BOG | 2019-02-20 | 0 | 1 | 1
19 | CB_16 | 19 | BOG | 2015-06-17 | 1 | 2 | 3
20 | CB_16 | 19 | BOG | 2015-12-12 | 1 | 2 | 3
21 | CB_16 | 19 | BOG | 2019-03-18 | 1 | 2 | 3
22 | CB_20 | 21 | BOG | 2011-08-26 | 1 | 0 | 1
23 | CB_20 | 21 | BOG | 2013-09-25 | 2 | 0 | 2
24 | CB_20 | 21 | BOG | 2019-01-11 | 3 | 1 | 2
25 | CB_20 | 21 | BOG | 2019-02-20 | 4 | 1 | 2
26 | CB_21 | 22 | BOG | 2011-08-26 | 0 | 0 | 1
27 | CB_21 | 22 | BOG | 2014-07-18 | 1 | 0 | 1
28 | CB_21 | 22 | BOG | 2019-02-20 | 1 | 0 | 1
29 | CB_23 | 23 | BOG | 2015-04-22 | 0 | 1 | 1
30 | CB_23 | 23 | BOG | 2015-12-12 | 1 | 1 | 2
31 | CB_23 | 23 | BOG | 2017-07-13 | 1 | 1 | 2
32 | CB_23 | 23 | BOG | 2019-03-18 | 1 | 1 | 2
33 | CB_24 | 24 | BOG | 2012-02-17 | 0 | 1 | 2
34 | CB_24 | 24 | BOG | 2015-06-18 | 0 | 1 | 0
35 | CB_24 | 24 | BOG | 2019-01-11 | 0 | 1 | 0
36 | CB_25 | 25 | BOG | 2011-08-26 | 1 | 2 | 1
37 | CB_25 | 25 | BOG | 2014-07-18 | 1 | 2 | 1
38 | CB_25 | 25 | BOG | 2019-01-11 | 1 | 2 | 1
39 | CB_25 | 25 | BOG | 2019-02-20 | 1 | 2 | 1
40 | CB_26 | 26 | BOG | 2015-04-22 | 0 | 2 | 2
41 | CB_26 | 26 | BOG | 2015-06-17 | 0 | 3 | 2
42 | CB_26 | 26 | BOG | 2018-06-21 | 0 | 2 | 2
43 | CB_26 | 26 | BOG | 2019-03-18 | 0 | 3 | 2
44 | CB_27 | 27 | BOG | 2012-02-17 | 1 | 0 | 2
45 | CB_27 | 27 | BOG | 2015-06-18 | 1 | 0 | 2
46 | CB_27 | 27 | BOG | 2017-07-17 | 1 | 0 | 2
47 | CB_27 | 27 | BOG | 2019-01-11 | 1 | 1 | 2
48 | CB_28 | 28 | BOG | 2011-08-26 | 1 | 0 | 1
49 | CB_28 | 28 | BOG | 2013-09-25 | 1 | 0 | 1
50 | CB_28 | 28 | BOG | 2014-07-18 | 1 | 0 | 1
51 | CB_28 | 28 | BOG | 2019-01-11 | 1 | 0 | 1
52 | CB_28 | 28 | BOG | 2019-02-20 | 1 | 0 | 2
53 | CB_29 | 29 | BOG | 2011-08-26 | 0 | 0 | 0
54 | CB_29 | 29 | BOG | 2019-02-20 | 1 | 2 | 0
55 | CB_31 | 30 | BOG | 2015-04-22 | 1 | 1 | 0
56 | CB_31 | 30 | BOG | 2015-06-17 | 1 | 1 | 0
57 | CB_31 | 30 | BOG | 2017-07-13 | 1 | 1 | 0
58 | CB_31 | 30 | BOG | 2018-06-21 | 1 | 1 | 2
59 | CB_31 | 30 | BOG | 2019-03-18 | 1 | 1 | 2
60 | CB_39 | 31 | BOG | 2013-09-06 | 1 | 1 | 1
61 | CB_39 | 31 | BOG | 2014-05-26 | 2 | 1 | 2
62 | CB_39 | 31 | BOG | 2017-07-17 | 2 | 1 | 2
63 | CB_39 | 31 | BOG | 2019-01-11 | 3 | 2 | 3

## _56F9DC9755BA473782653E2940F9 (hidden)
2MF_VyIJjkWHv-xPRV62AFp6FmJGvDJDlaNXvDlwm8NUQVQ5TFVKRllOUTRMWlBJS0syOUhLSFNOVi4u
Form1
{dcbd5c6e-e310-4cb1-a15e-380c47f2a6be}