## Instrucciones
Bienvenido al sistema SAMS | Modulo Transformadores
Av, Carrera 30 No.45-03 Edifico 614 Bogotá D.C. (571) 316 5000 Ext. 11000

## TR
Load | Temp | Type | ID | Serial | Location | Opt_Year | Brand | Model | U_max | S | I_LV | Paper_Therm_Up | Oil | ONAF_I | ONAF_II | Top_Oil | Avg_Wing | Ta | Material | Windings | Phases | Connection | Z | Oil_Litters | Mass_Core | Mass_Tank | Po | i2R | Stray_Losses | Eddy_Losses | Top_Oil | Bot_Oil | Avg_Wing | dTheta_TO_R | Gradient | UC
TR1 | 25 | TR | TR_1 | 1 | BOG_1 | 1993 | Siemens | AT | 345 | 700 | 24.52 | FALSE | Mineral | 1.25 | 1.5 | 55 | 19.6 | 2.5 | Cooper | 2 | 3 | YNy0 | 0.1306 | 855 | 245 | 132 | 0 | 0 | 0 | 0 | 55 | 33 | 60 | 0 | 14.85 | N5S2
TR2 | 25 | TR | TR_2 | 2 | BOG_2 | 1993 | Siemens | AT | 345 | 1000 | 35.03 | FALSE | Mineral | 1.25 | 1.5 | 55 | 19.6 | 2.5 | Cooper | 2 | 3 | YNy0 | 0.1306 | 1083 | 424 | 156 | 0 | 0 | 0 | 0 | 55 | 33 | 60 | 0 | 14.85 | N5S2
TR3 | 25 | TR | TR_3 | 3 | BOG_3 | 1993 | Siemens | AT | 345 | 1000 | 35.03 | FALSE | Mineral | 1.25 | 1.5 | 55 | 19.6 | 2.5 | Cooper | 2 | 3 | YNy0 | 0.175 | 1083 | 424 | 156 | 0 | 0 | 0 | 0 | 55 | 33 | 60 | 0 | 14.85 | N5S2
TR4 | 25 | TR | TR_4 | 4 | BOG_4 | 1993 | Siemens | AT | 345 | 800 | 28.02 | FALSE | Mineral | 1.25 | 1.5 | 55 | 19.6 | 2.5 | Cooper | 2 | 3 | YNy0 | 0.16 | 925 | 312 | 145 | 0 | 0 | 0 | 0 | 55 | 33 | 60 | 0 | 14.85 | N5S2
TR5 | 25 | TR | TR_5 | 5 | BOG_5 | 1993 | Siemens | AT | 345 | 700 | 24.52 | FALSE | Mineral | 1.25 | 1.5 | 55 | 19.6 | 0 | Cooper | 2 | 3 | YNy0 | 0.1137 | 855 | 245 | 132 | 0 | 0 | 0 | 0 | 55 | 33 | 60 | 0 | 14.85 | N5S2
TR6 | 25 | TR | TR_6 | 6 | BOG_6 | 1993 | Siemens | AT | 345 | 800 | 28.02 | FALSE | Mineral | 1.25 | 1.5 | 55 | 19.6 | 3.5 | Cooper | 2 | 3 | YNy0 | 0.1081 | 925 | 312 | 145 | 0 | 0 | 0 | 0 | 55 | 33 | 60 | 0 | 14.85 | N5S2
TR7 | 25 | TR | TR_7 | 7 | BOG_7 | 1993 | Siemens | AT | 345 | 1000 | 2.51 | FALSE | Mineral | 1.25 | 1.5 | 55 | 19.6 | 3 | Cooper | 2 | 3 | YNy0 | 0.1144 | 1083 | 424 | 156 | 0 | 0 | 0 | 0 | 55 | 33 | 60 | 0 | 14.85 | N5S2
TR8 | 25 | TR | TR_8 | 8 | BOG_8 | 1993 | Siemens | AT | 230 | 600 | 21.01 | FALSE | Mineral | 1.25 | 1.5 | 55 | 19.6 | 0.9 | Cooper | 2 | 3 | YNy0 | 0.1904 | 739 | 232 | 116 | 0 | 0 | 0 | 0 | 55 | 33 | 60 | 0 | 14.85 | N5S2
TR9 | 25 | TR | TR_9 | 9 | BOG_9 | 1993 | Siemens | AT | 345 | 300 | 1.25 | FALSE | Mineral | 1.25 | 1.5 | 55 | 19.6 | 0.6 | Cooper | 2 | 3 | YNy0 | 0.1625 | 462 | 110 | 98 | 0 | 0 | 0 | 0 | 55 | 33 | 60 | 0 | 14.85 | N5S2
TR10 | 25 | TR | TR_10 | 10 | BOG_10 | 1993 | Siemens | AT | 345 | 800 | 28.02 | FALSE | Mineral | 1.25 | 1.5 | 55 | 19.6 | 3.5 | Cooper | 2 | 3 | YNy0 | 0.181 | 925 | 312 | 145 | 0 | 0 | 0 | 0 | 55 | 33 | 60 | 0 | 14.85 | N5S2
TR11 | 25 | TR | TR_11 | 11 | BOG_11 | 1993 | Siemens | AT | 345 | 300 | 1.25 | FALSE | Mineral | 1.25 | 1.5 | 55 | 19.6 | 0.6 | Cooper | 2 | 3 | YNy0 | 0.1562 | 462 | 110 | 98 | 0 | 0 | 0 | 0 | 55 | 33 | 60 | 0 | 14.85 | N5S2
TR12 | 25 | TR | TR_12 | 12 | BOG_12 | 1993 | Siemens | AT | 345 | 700 | 24.52 | FALSE | Mineral | 1.25 | 1.5 | 55 | 19.6 | 3.5 | Cooper | 2 | 3 | YNy0 | 0.1382 | 855 | 245 | 132 | 0 | 0 | 0 | 0 | 55 | 33 | 60 | 0 | 14.85 | N5S2

## DGA
Test_ID | Pos | Serial | Location | Date | H | O | N | CO | CH4 | CO2 | C2H4 | C2H6 | C2H2 | TDCG
1 | TR_1 | 1 | Bog | 2015-03-18 | 0.57067 | 2415.335 | 5533.374 | 3.0872 | 0 | 41.7234 | 0 | 0 | 0 | 44.8106
2 | TR_1 | 1 | Bog | 2015-04-17 | 0.82105 | 4584.237 | 10761.9 | 7.2413 | 0 | 85.6772 | 0 | 0 | 0 | 92.9185
3 | TR_1 | 1 | Bog | 2015-04-22 | 1.8923 | 5461.517 | 13580.86 | 10.2169 | 0.40351 | 105.828 | 0 | 0 | 0 | 116.4484
4 | TR_1 | 1 | Bog | 2015-12-09 | 2.3899 | 3848.962 | 12761.75 | 30.0782 | 0 | 145.6121 | 0 | 0 | 0 | 175.6903
5 | TR_1 | 1 | Bog | 2016-06-16 | 4.0084 | 10262.94 | 37083.49 | 95.4701 | 0 | 405.5897 | 0 | 0 | 0 | 501.0598
6 | TR_1 | 1 | Bog | 2017-05-04 | 10.1757 | 9694.103 | 31035.57 | 107.5745 | 1.3206 | 393.0207 | 0 | 0 | 0 | 501.9158
7 | TR_1 | 1 | Bog | 2018-02-26 | 8.3853 | 17028.45 | 39088.48 | 157.1902 | 2.2192 | 565.6402 | 0.22508 | 0.91685 | 0 | 726.1915
8 | TR_2 | 2 | Bog | 2007-01-22 | 31.1792 | 18586.15 | 38981.54 | 82.288 | 6.8634 | 1147.982 | 12.0949 | 1.025 | 96.3539 | 1346.6072
9 | TR_2 | 2 | Bog | 2007-02-06 | 28.4944 | 16201.13 | 34120 | 70.3635 | 6.222 | 1082.572 | 11.7269 | 0.70742 | 96.3708 | 1267.9625
10 | TR_2 | 2 | Bog | 2007-04-09 | 30.4279 | 17113.73 | 39527.61 | 72.5519 | 7.6095 | 1281.556 | 14.2476 | 1.354 | 145.6573 | 1522.9763
11 | TR_2 | 2 | Bog | 2007-04-24 | 31.0297 | 18535.05 | 39992.83 | 67.3507 | 8.0545 | 1269.502 | 15.8339 | 1.5511 | 146.6431 | 1508.9353
12 | TR_2 | 2 | Bog | 2007-05-16 | 32.7298 | 17171.66 | 40631.14 | 67.183 | 8.4529 | 1300.704 | 16.3172 | 1.5722 | 158.7835 | 1553.0127
13 | TR_2 | 2 | Bog | 2007-06-22 | 33.8229 | 18569.83 | 43417.21 | 74.054 | 8.9826 | 1405.558 | 17.8033 | 1.7852 | 162.2863 | 1670.4694
14 | TR_2 | 2 | Bog | 2007-07-06 | 31.8801 | 18487.59 | 42721.2 | 70.9453 | 8.8377 | 1408.122 | 18.5767 | 1.904 | 167.1672 | 1675.5529
15 | TR_2 | 2 | Bog | 2007-09-11 | 27.4051 | 14225.96 | 32385.48 | 62.2589 | 7.0616 | 1219.61 | 15.8614 | 1.5832 | 152.9844 | 1459.3594
16 | TR_2 | 2 | Bog | 2007-12-13 | 25.9656 | 15067.54 | 36020.55 | 67.9608 | 7.6814 | 1098.592 | 18.3151 | 1.7642 | 156.9507 | 1351.2642
17 | TR_2 | 2 | Bog | 2008-04-24 | 28.1053 | 17380.62 | 43368.37 | 73.7785 | 8.4242 | 1310.439 | 18.3718 | 2.4184 | 184.1459 | 1597.5777
18 | TR_2 | 2 | Bog | 2008-05-22 | 20.6258 | 17682.55 | 40756.4 | 66.0841 | 7.308 | 1269.509 | 19.568 | 1.9636 | 175.0419 | 1539.4746
19 | TR_2 | 2 | Bog | 2008-06-16 | 17.9449 | 17011.15 | 38795.5 | 59.0381 | 5.9934 | 1210.553 | 15.543 | 1.5739 | 147.9752 | 1440.6766
20 | TR_2 | 2 | Bog | 2008-08-20 | 11.6748 | 17935.81 | 44100.82 | 69.2386 | 5.2133 | 1323.451 | 14.8343 | 1.4612 | 149.5574 | 1563.7557
21 | TR_2 | 2 | Bog | 2008-12-09 | 10.1966 | 18085.36 | 42964.14 | 74.7904 | 4.0763 | 1477.29 | 17.0543 | 1.8672 | 156.8506 | 1731.9289
22 | TR_2 | 2 | Bog | 2009-03-20 | 11.0438 | 17529.16 | 43302.61 | 98.7977 | 3.7742 | 1563.81 | 14.1552 | 1.5732 | 144.1281 | 1826.2384
23 | TR_2 | 2 | Bog | 2010-04-26 | 15.7617 | 19155.04 | 47255.63 | 108.3558 | 4.4209 | 1704.202 | 13.8298 | 1.6115 | 78.3489 | 1910.7689
24 | TR_2 | 2 | Bog | 2010-11-08 | 17.377 | 18592.7 | 43485.28 | 65.1475 | 4.0652 | 1577.711 | 12.6088 | 1.5255 | 83.2184 | 1744.2763
25 | TR_2 | 2 | Bog | 2011-12-01 | 18.9872 | 18690.34 | 42710.61 | 55.0992 | 4.5466 | 1282.835 | 12.4342 | 1.6948 | 78.093 | 1434.7028
26 | TR_2 | 2 | Bog | 2013-05-16 | 6.2346 | 18020.19 | 43032.46 | 51.1489 | 1.6442 | 1103.308 | 5.8288 | 0.21467 | 29.8609 | 1192.0055
27 | TR_2 | 2 | Bog | 2014-03-31 | 5.4686 | 20060.42 | 43713.61 | 0 | 0.001 | 1017.068 | 5.9486 | 1.0234 | 28.1911 | 1052.2321
28 | TR_2 | 2 | Bog | 2015-06-03 | 7.356 | 18935.04 | 42720.09 | 53.6182 | 1.8091 | 978.1443 | 4.4552 | 0.99664 | 20.1442 | 1059.1676
29 | TR_2 | 2 | Bog | 2016-07-06 | 8.3734 | 18091.69 | 46939.96 | 55.6828 | 0 | 1079.953 | 9.1887 | 26.2973 | 15.502 | 1186.6238
30 | TR_2 | 2 | Bog | 2017-05-10 | 12.6905 | 11520.18 | 50781 | 89.3315 | 2.3693 | 1346.888 | 5.2542 | 2.4007 | 16.0312 | 1462.2749
31 | TR_2 | 2 | Bog | 2018-08-24 | 4.3974 | 5981.839 | 4516.491 | 13.74 | 0 | 1335.472 | 1.5996 | 1.5863 | 0 | 1352.3979
32 | TR_3 | 3 | Bog | 2006-12-07 | 16.0543 | 227.5273 | 37139.94 | 178.1887 | 24.0985 | 1155.681 | 2.196 | 41.3313 | 0.16853 | 1401.664
33 | TR_3 | 3 | Bog | 2009-01-19 | 5.6214 | 225.7021 | 29393.59 | 117.8854 | 20.2602 | 651.3934 | 2.2034 | 19.5278 | 0 | 811.2701
34 | TR_3 | 3 | Bog | 2010-02-12 | 6.7113 | 611.5819 | 41202.86 | 127.172 | 47.1748 | 926.9664 | 4.5388 | 80.3126 | 0 | 1186.1646
35 | TR_3 | 3 | Bog | 2011-06-14 | 7.8546 | 1792.865 | 50514.98 | 120.7239 | 62.0471 | 983.8198 | 5.1231 | 133.6079 | 0 | 1305.3217
36 | TR_3 | 3 | Bog | 2012-08-13 | 7.4287 | 940.6993 | 54423.38 | 102.6991 | 50.1789 | 954.2174 | 4.5193 | 141.2202 | 0.001 | 1252.8359
37 | TR_3 | 3 | Bog | 2013-08-15 | 8.5481 | 1124.718 | 46711.25 | 123.5973 | 51.8198 | 1086.849 | 5.6464 | 132.0541 | 0.001 | 1399.9676
38 | TR_3 | 3 | Bog | 2014-07-08 | 5.2055 | 616.4627 | 48124.52 | 193.422 | 65.7686 | 1445.79 | 7.0255 | 141.3501 | 0.001 | 1853.3573
39 | TR_3 | 3 | Bog | 2015-02-17 | 6.9966 | 3048.873 | 55310.03 | 225.3375 | 71.6919 | 1555.789 | 6.6491 | 130.342 | 0 | 1989.8095
40 | TR_3 | 3 | Bog | 2017-03-24 | 8.1888 | 291.3712 | 48380 | 260.0658 | 77.957 | 1850.702 | 14.9847 | 128.0477 | 0 | 2331.7571
41 | TR_3 | 3 | Bog | 2018-08-27 | 0 | 1117.799 | 8615.079 | 27.6546 | 8.2075 | 1261.161 | 1.9006 | 17.6234 | 0 | 1316.5471
42 | TR_4 | 4 | Bog | 2008-05-14 | 605.1365 | 14792.12 | 35041.42 | 63.3831 | 2.7673 | 644.1664 | 0.34415 | 0.83295 | 1.1409 | 712.6347
43 | TR_4 | 4 | Bog | 2008-06-16 | 840.2386 | 17078.43 | 40451.25 | 76.7651 | 3.1125 | 757.6471 | 0.28415 | 0.85884 | 1.178 | 839.8457
44 | TR_4 | 4 | Bog | 2008-11-21 | 996.8235 | 14933.21 | 34582.56 | 75.0475 | 3.1811 | 746.0823 | 0.40983 | 1.0227 | 0.86232 | 826.6057
45 | TR_4 | 4 | Bog | 2009-01-13 | 885.8959 | 17264.65 | 41908.88 | 84.8996 | 3.4248 | 837.1787 | 0.55452 | 1.3364 | 1.0277 | 928.4217
46 | TR_4 | 4 | Bog | 2009-06-03 | 704.4802 | 15796.93 | 35720.09 | 84.4727 | 2.5411 | 878.3938 | 0.25559 | 0.84722 | 0.34725 | 966.8576
47 | TR_4 | 4 | Bog | 2010-05-20 | 264.3086 | 14140.36 | 31910.22 | 80.4462 | 1.5773 | 773.7996 | 0.47829 | 0.72075 | 0.85974 | 857.8819
48 | TR_4 | 4 | Bog | 2012-08-14 | 60.8231 | 16646.87 | 44544.41 | 82.5591 | 1.4958 | 751.6069 | 0.99047 | 0.53616 | 0.001 | 837.1894
49 | TR_4 | 4 | Bog | 2014-09-18 | 19.3769 | 17572.91 | 37355.32 | 67.1502 | 0.001 | 941.6304 | 0.74088 | 0.001 | 0.001 | 1009.5245
50 | TR_4 | 4 | Bog | 2017-03-13 | 11.5209 | 15016.09 | 37271.44 | 83.5626 | 1.1679 | 932.4609 | 1.2851 | 0 | 0 | 1018.4765
51 | TR_4 | 4 | Bog | 2018-02-13 | 12.9243 | 23576.7 | 43835.41 | 106.6403 | 2.0385 | 1039.713 | 2.6677 | 1.4249 | 2.0535 | 1154.5379
52 | TR_5 | 5 | Bog | 2008-04-10 | 6.4669 | 734.1814 | 42993.47 | 719.5331 | 24.7025 | 2166.295 | 27.0512 | 18.7071 | 0 | 2956.289
53 | TR_5 | 5 | Bog | 2009-01-13 | 5.4969 | 2357.964 | 42962.85 | 691.4864 | 21.2182 | 2276.462 | 6.1142 | 6.5947 | 0 | 3001.8755
54 | TR_5 | 5 | Bog | 2010-12-07 | 5.5417 | 4017.602 | 44603.01 | 550.652 | 15.1631 | 1862.677 | 6.1669 | 6.3938 | 0 | 2441.0529
55 | TR_5 | 5 | Bog | 2012-03-21 | 3.4222 | 2711.522 | 56338.47 | 634.9048 | 17.638 | 1670.447 | 6.5514 | 7.318 | 0.001 | 2336.8603
56 | TR_5 | 5 | Bog | 2013-03-22 | 6.8584 | 1738.868 | 59378.59 | 593.1543 | 25.7164 | 1187.923 | 6.8005 | 6.4318 | 0.001 | 1820.027
57 | TR_5 | 5 | Bog | 2014-02-27 | 6.8919 | 2692.396 | 49834.59 | 869.3909 | 34.8169 | 3947.604 | 1.163 | 5.344 | 0.001 | 4858.3198
58 | TR_5 | 5 | Bog | 2015-06-02 | 8.0757 | 1412.336 | 47458.26 | 937.0078 | 41.5455 | 3327.167 | 6.0735 | 8.4303 | 0 | 4320.2242
59 | TR_5 | 5 | Bog | 2016-10-24 | 9.0318 | 602.4737 | 48616.23 | 907.9929 | 44.7789 | 3850.569 | 9.2326 | 8.9579 | 0 | 4821.5314
60 | TR_5 | 5 | Bog | 2017-08-17 | 7.2419 | 3636.219 | 59678.66 | 754.7604 | 25.231 | 2785.727 | 5.251 | 7.8391 | 0 | 3578.8085
61 | TR_5 | 5 | Bog | 2018-02-07 | 15.6639 | 318.115 | 47128.32 | 920.1265 | 42.9222 | 3897.082 | 10.0691 | 13.1722 | 4.7377 | 4888.1097
62 | TR_6 | 6 | Bog | 2016-07-08 | 0 | 715.3235 | 1664.754 | 0 | 0 | 12.6356 | 0.075934 | 0.79789 | 0 | 13.5094
63 | TR_6 | 6 | Bog | 2017-02-14 | 2.1853 | 7769.817 | 31996.91 | 76.8022 | 0 | 320.2974 | 0 | 0 | 0.77276 | 397.8723
64 | TR_6 | 6 | Bog | 2018-08-28 | 27.0513 | 2722.885 | 799.6265 | 55.8815 | 3.5174 | 912.0278 | 3.2203 | 0.63669 | 7.5479 | 982.8317
65 | TR_7 | 7 | Bog | 2012-03-22 | 15.0427 | 930.4285 | 5550.714 | 85.4771 | 0.91339 | 199.3983 | 0.001 | 0.11863 | 0.001 | 285.9094
66 | TR_7 | 7 | Bog | 2013-03-22 | 21.4751 | 1540.337 | 9798.801 | 124.9437 | 2.4525 | 188.74 | 0.11341 | 0.27416 | 0.001 | 316.5248
67 | TR_7 | 7 | Bog | 2014-02-21 | 48.8778 | 0 | 20984.36 | 447.3918 | 6.1633 | 1119.374 | 0.43398 | 0.77542 | 0.001 | 1574.1395
68 | TR_7 | 7 | Bog | 2015-06-02 | 16.8383 | 1927.316 | 10794.84 | 272.599 | 4.0742 | 683.5308 | 0.35906 | 0.65044 | 0 | 961.2135
69 | TR_7 | 7 | Bog | 2017-03-08 | 9.833 | 2066.197 | 13048.93 | 334.4065 | 5.0114 | 854.8615 | 0.34477 | 1.5678 | 0 | 1196.192
70 | TR_7 | 7 | Bog | 2018-08-31 | 4.2541 | 4545.225 | 1194.825 | 76.6561 | 0 | 1371.887 | 0 | 0 | 0 | 1448.5431
71 | TR_8 | 8 | Bog | 2007-02-05 | 6.6869 | 10393.37 | 33238.25 | 164.5586 | 1.5375 | 1000.354 | 19.7477 | 0.77661 | 0 | 1186.9744
72 | TR_8 | 8 | Bog | 2007-12-07 | 11.031 | 6640.789 | 34996.29 | 199.1488 | 2.2846 | 1083.564 | 24.8682 | 1.2712 | 0 | 1311.1368
73 | TR_8 | 8 | Bog | 2008-12-02 | 11.0361 | 2330.993 | 42401.61 | 192.7157 | 7.8388 | 1179.794 | 17.1032 | 2.8972 | 0 | 1400.3489
74 | TR_8 | 8 | Bog | 2009-06-19 | 13.0401 | 673.8171 | 38419.43 | 187.3289 | 12.7054 | 945.1889 | 10.1029 | 5.4025 | 0 | 1160.7287
75 | TR_8 | 8 | Bog | 2010-12-07 | 12.7143 | 602.6677 | 27925.17 | 121.4278 | 10.1739 | 701.1478 | 4.6504 | 7.4882 | 0 | 844.8881
76 | TR_8 | 8 | Bog | 2011-12-15 | 18.3812 | 1173.053 | 52797.78 | 180.5853 | 13.4468 | 1002.06 | 5.3384 | 10.9547 | 0 | 1212.3852
77 | TR_8 | 8 | Bog | 2013-04-05 | 23.3926 | 1476.479 | 47589.78 | 198.2486 | 8.1662 | 1030.146 | 3.1969 | 8.5489 | 0.001 | 1248.3077
78 | TR_8 | 8 | Bog | 2014-02-13 | 25.4684 | 1800.947 | 40820.71 | 213.9879 | 9.2058 | 1168.596 | 21.0422 | 18.3145 | 0.001 | 1431.1475
79 | TR_8 | 8 | Bog | 2016-04-18 | 25.7819 | 2528.696 | 47031.91 | 253.2171 | 11.2028 | 1600.343 | 6.8015 | 9.1717 | 0 | 1880.7361
80 | TR_8 | 8 | Bog | 2017-01-03 | 35.9382 | 2277.408 | 42930.47 | 267.7003 | 9.1131 | 1509.331 | 6.927 | 10.0323 | 0 | 1803.1037
81 | TR_8 | 8 | Bog | 2018-02-12 | 28.1231 | 988.8392 | 21284.34 | 138.8133 | 3.3424 | 867.1017 | 2.1455 | 3.198 | 0 | 1014.601
82 | TR_9 | 9 | Bog | 2008-11-21 | 0 | 1011.584 | 3346.944 | 3.0472 | 0 | 23.8436 | 0 | 0 | 0 | 26.8909
83 | TR_9 | 9 | Bog | 2009-03-02 | 3.9403 | 2240.068 | 9711.058 | 60.1198 | 0.61983 | 215.4634 | 0.14764 | 0 | 0 | 276.3506
84 | TR_9 | 9 | Bog | 2009-11-13 | 6.9736 | 1558.975 | 9290.076 | 131.7033 | 1.8042 | 365.0706 | 0.90635 | 0.117 | 0 | 499.6015
85 | TR_9 | 9 | Bog | 2010-04-12 | 6.7781 | 1264.631 | 8049.544 | 132.4544 | 1.6861 | 353.8481 | 0.2824 | 0 | 0 | 488.271
86 | TR_9 | 9 | Bog | 2011-11-04 | 15.143 | 1372.323 | 11573.08 | 216.8222 | 2.5795 | 623.507 | 0.34547 | 0.19366 | 0 | 843.4478
87 | TR_9 | 9 | Bog | 2012-02-02 | 13.208 | 1133.248 | 7100.258 | 141.1827 | 1.9992 | 309.2996 | 0.19749 | 0.14367 | 0 | 452.8226
88 | TR_9 | 9 | Bog | 2013-05-15 | 17.2906 | 1925.542 | 19081.6 | 296.5547 | 5.5519 | 587.826 | 0.56332 | 0.41152 | 0.001 | 890.9085
89 | TR_9 | 9 | Bog | 2014-03-27 | 7.3729 | 1931.905 | 15815.52 | 259.2068 | 3.2282 | 496.3365 | 0.38926 | 0.18703 | 0.001 | 759.3488
90 | TR_9 | 9 | Bog | 2016-06-16 | 3.7864 | 1389.995 | 23065.78 | 445.6886 | 8.4684 | 1886.66 | 1.0903 | 1.2668 | 0 | 2343.1741
91 | TR_9 | 9 | Bog | 2017-04-11 | 6.232 | 1212.655 | 26332.3 | 504.3299 | 9.1698 | 1895.126 | 0.96238 | 0.58798 | 0 | 2410.176
92 | TR_9 | 9 | Bog | 2018-06-13 | 2.5507 | 19.2612 | 23588.72 | 323.0881 | 9.291 | 1094.643 | 1.576 | 1.7189 | 0 | 1430.317
93 | TR_10 | 10 | Bog | 2007-03-13 | 8.2003 | 294.5458 | 41097.28 | 388.9458 | 18.6934 | 1384.601 | 4.0452 | 5.0552 | 0 | 1801.3406
94 | TR_10 | 10 | Bog | 2009-01-15 | 6.4863 | 543.2584 | 49093.18 | 449.7455 | 23.2381 | 1596.312 | 5.1853 | 4.6078 | 0 | 2079.0887
95 | TR_10 | 10 | Bog | 2011-09-14 | 6.6233 | 1306.817 | 61921.07 | 467.2656 | 26.8314 | 2082.876 | 5.1974 | 5.8862 | 0 | 2588.0566
96 | TR_10 | 10 | Bog | 2013-08-16 | 7.5089 | 2506.333 | 55005.37 | 497.4545 | 28.2413 | 2189.36 | 5.4693 | 5.6051 | 0.001 | 2726.1312
97 | TR_10 | 10 | Bog | 2014-07-09 | 0.001 | 948.9995 | 54305.37 | 548.6104 | 31.5382 | 2471.576 | 6.9316 | 7.0718 | 0.001 | 3065.729
98 | TR_10 | 10 | Bog | 2016-07-08 | 6.1727 | 739.2157 | 50959.91 | 481.7036 | 37.6717 | 2330.344 | 5.1957 | 8.4564 | 0 | 2863.3715
99 | TR_10 | 10 | Bog | 2017-04-24 | 5.1689 | 351.1825 | 59638.66 | 546.5277 | 42.2176 | 2333.119 | 6.7726 | 15.2413 | 0 | 2943.8782
100 | TR_10 | 10 | Bog | 2018-10-09 | 3.3741 | 4744.957 | 16918.99 | 33.1226 | 3.9523 | 404.8944 | 3.114 | 0 | 0 | 445.0834
101 | TR_11 | 11 | Bog | 2007-07-06 | 4.0837 | 12033.54 | 33062.88 | 238.2952 | 1.5938 | 1008.462 | 44.8258 | 0.49231 | 41.2725 | 1334.9416
102 | TR_11 | 11 | Bog | 2007-11-20 | 5.8248 | 13451.28 | 38077.1 | 274.9055 | 1.7256 | 1197.732 | 52.2792 | 0.69923 | 44.6668 | 1572.0084
103 | TR_11 | 11 | Bog | 2008-03-26 | 6.7065 | 13503.3 | 40556.47 | 349.1415 | 2.0722 | 1258.055 | 56.666 | 0.54573 | 43.2481 | 1709.7286
104 | TR_11 | 11 | Bog | 2008-12-18 | 3.2911 | 12556.72 | 36208.68 | 309.3794 | 1.9186 | 1215.509 | 69.8917 | 0.53851 | 36.6225 | 1633.8597
105 | TR_11 | 11 | Bog | 2009-01-16 | 3.8975 | 12361.57 | 34317.93 | 285.2226 | 1.741 | 1169.576 | 65.9723 | 0.54639 | 33.7878 | 1556.846
106 | TR_11 | 11 | Bog | 2010-02-15 | 2.8034 | 13424.02 | 37762.17 | 264.3158 | 1.5656 | 1070.347 | 66.8061 | 0.43206 | 16.8474 | 1420.314
107 | TR_11 | 11 | Bog | 2012-09-20 | 3.6824 | 13305.37 | 38157.13 | 258.7227 | 1.6275 | 1044.756 | 78.5075 | 0.32104 | 17.5407 | 1401.4754
108 | TR_11 | 11 | Bog | 2014-04-22 | 3.154 | 15537.48 | 45410.18 | 273.8176 | 0.001 | 1496.277 | 130.6414 | 0.49939 | 27.5131 | 1928.7495
109 | TR_11 | 11 | Bog | 2015-06-03 | 4.203 | 14066.86 | 43098.93 | 381.5575 | 2.2926 | 1640.469 | 149.2978 | 0 | 17.3348 | 2190.9517
110 | TR_11 | 11 | Bog | 2016-04-20 | 0 | 11398.01 | 41076.52 | 362.7634 | 1.912 | 1651.711 | 139.1651 | 0.22892 | 8.5146 | 2164.295
111 | TR_11 | 11 | Bog | 2017-02-15 | 1.7786 | 6317.995 | 23873.3 | 227.4724 | 1.7332 | 1181.777 | 88.4121 | 0.74488 | 2.7951 | 1502.9347
112 | TR_12 | 12 | Bog | 2007-04-11 | 1.5954 | 17369.49 | 38826.11 | 73.7421 | 0.70056 | 772.9847 | 8.1566 | 0 | 0 | 855.584
113 | TR_12 | 12 | Bog | 2009-03-02 | 1.8322 | 16509.45 | 38454.59 | 82.4242 | 0.74821 | 810.3838 | 7.4842 | 0 | 0 | 901.0404
114 | TR_12 | 12 | Bog | 2010-11-08 | 2.1769 | 18960.82 | 46227.8 | 86.6796 | 0.91077 | 933.8834 | 10.073 | 0 | 0 | 1031.5467
115 | TR_12 | 12 | Bog | 2011-10-08 | 1.9841 | 19176.38 | 39333.89 | 64.5676 | 0.76235 | 618.9166 | 7.6998 | 0 | 0 | 691.9464
116 | TR_12 | 12 | Bog | 2011-12-02 | 3.0654 | 18259.2 | 43604.14 | 76.6142 | 0.81878 | 705.2609 | 8.1825 | 0 | 0 | 790.8764
117 | TR_12 | 12 | Bog | 2013-03-22 | 4.3011 | 15594.73 | 51116.88 | 122.8928 | 1.3421 | 842.6747 | 11.9987 | 0.1042 | 0.001 | 979.0135
118 | TR_12 | 12 | Bog | 2014-02-07 | 4.4699 | 17251.28 | 44266.39 | 126.83 | 0.001 | 991.72 | 13.1411 | 7.451 | 0.001 | 1139.1441
119 | TR_12 | 12 | Bog | 2017-01-04 | 4.6633 | 15004.87 | 50861.6 | 209.0096 | 0 | 2186.832 | 17.3882 | 0 | 0 | 2413.2298
120 | TR_12 | 12 | Bog | 2018-11-01 | 311.4855 | 25926.74 | 80139.53 | 195.9401 | 0 | 160.7584 | 0 | 0 | 0 | 356.6985
Note on N1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Todas las concentraciones de gases deben ir en ppm
Note on O1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Todas las concentraciones de gases deben ir en ppm

## PQ
Test_ID | Pos | Serial | Location | Date | C_H2O | Sat | Color | IT | DS | AN
1 | TR_1 | 1 | Bog | 2015-03-19 | 4.9 | 9 | 0.5 | 46.1525 | 39.9 | 0.013
2 | TR_1 | 1 | Bog | 2015-04-27 | 3.3 | 3 | 0.5 | 42.8367 | 46.48 | 0.01
3 | TR_1 | 1 | Bog | 2015-04-27 | 2.7 | 3 | 0.5 | 41.7466 | 39.42 | 0.015
4 | TR_1 | 1 | Bog | 2015-12-09 | 2.5 | 2 | 0.5 | 40.4658 | 51.98 | 0.009
5 | TR_1 | 1 | Bog | 2016-06-21 | 3.8 | 3 | 0.5 | 45.1993 | 46.18 | 0.004
6 | TR_1 | 1 | Bog | 2017-05-08 | 8.1 | 7 | 0.5 | 47.1653 | 29.06 | 0.005
7 | TR_1 | 1 | Bog | 2018-03-01 | 2.7 | 2 | 0.5 | 37.7674 | 51.34 | 0.005
8 | TR_1 | 1 | Bog | 2019-03-18 | 3.7 | 4.101 | 0.5 | 38.55 | 33.3 | 0.006
9 | TR_2 | 2 | Bog | 2007-01-23 | 8.1 | 7 | 1 | 29.5504 | 34.46 | 0.009
10 | TR_2 | 2 | Bog | 2008-05-21 | 8.3 | 7 | 1 | 31.4985 | 33.22 | 0.009
11 | TR_2 | 2 | Bog | 2008-08-26 | 7.9 | 7 | 1 | 30.1513 | 41.58 | 0.01
12 | TR_2 | 2 | Bog | 2009-04-30 | 11.9 | 8 | 1.5 | 29.8074 | 36 | 0.017
13 | TR_2 | 2 | Bog | 2010-04-27 | 14.3 | 10 | 1.5 | 26.7033 | 35.04 | 0.018
14 | TR_2 | 2 | Bog | 2011-12-14 | 9.3 | 8 | 1.5 | 27.7908 | 39.64 | 0.014
15 | TR_2 | 2 | Bog | 2013-05-30 | 9.5 | 6 | 1.5 | 29.2073 | 39.88 | 0.018
16 | TR_2 | 2 | Bog | 2014-04-21 | 9.5 | 8 | 1.5 | 27.3309 | 44.4 | 0.016
17 | TR_2 | 2 | Bog | 2015-06-11 | 9.1 | 8 | 1.5 | 27.8563 | 35.64 | 0.038
18 | TR_2 | 2 | Bog | 2016-07-06 | 10.8 | 8 | 1.5 | 26.1158 | 29.5 | 0.017
19 | TR_2 | 2 | Bog | 2017-05-11 | 10.1 | 8 | 1.5 | 29.2181 | 20.62 | 0.02
20 | TR_3 | 3 | Bog | 2006-12-11 | 5.4 | 4 | 1.5 | 37.6563 | 46.9
21 | TR_3 | 3 | Bog | 2009-02-02 | 8.2 | 5 | 2 | 28.101 | 44.56 | 0.025
22 | TR_3 | 3 | Bog | 2010-02-23 | 7.9 | 5 | 2 | 28.359 | 38.34 | 0.029
23 | TR_3 | 3 | Bog | 2011-07-07 | 7 | 4 | 2.5 | 27.9076 | 49.32 | 0.023
24 | TR_3 | 3 | Bog | 2012-08-22 | 7.1 | 5 | 3 | 26.5268 | 44.12 | 0.03
25 | TR_3 | 3 | Bog | 2013-08-01 | 9 | 6 | 3 | 26.9816 | 47.52 | 0.031
26 | TR_3 | 3 | Bog | 2014-07-15 | 10 | 4 | 3.5 | 26.0093 | 50.28 | 0.041
27 | TR_3 | 3 | Bog | 2015-02-25 | 10.6 | 4 | 3.5 | 24.8974 | 46.56 | 0.043
28 | TR_3 | 3 | Bog | 2017-04-04 | 11.8 | 5 | 4.5 | 24.3388 | 40.7 | 0.058
29 | TR_3 | 3 | Bog | 2018-02-21 | 13.6 | 8 | 4.5 | 23.4811 | 37.84 | 0.062
30 | TR_3 | 3 | Bog | 2019-02-20 | 12 | 7.6065 | 5 | 23.82 | 33.3 | 0.054
31 | TR_4 | 4 | Bog | 2008-05-08 | 8.4 | 10 | 0.5 | 41.6091 | 28.38 | 0.004
32 | TR_4 | 4 | Bog | 2008-11-25 | 8.7 | 11 | 0.5 | 42.3141 | 50.34 | 0.004
33 | TR_4 | 4 | Bog | 2009-01-21 | 9.1 | 8 | 0.5 | 38.9269 | 46.96 | 0.004
34 | TR_4 | 4 | Bog | 2010-05-21 | 9.5 | 8 | 0.5 | 36.5288 | 44.28 | 0.004
35 | TR_4 | 4 | Bog | 2012-08-28 | 10 | 8 | 0.5 | 38.7073 | 48.58 | 0.005
36 | TR_4 | 4 | Bog | 2014-09-15 | 9.4 | 8 | 0.5 | 41.9666 | 38.86 | 0.01
37 | TR_4 | 4 | Bog | 2017-03-29 | 9.8 | 12 | 0.5 | 41.0281 | 44.5 | 0.01
38 | TR_4 | 4 | Bog | 2018-02-28 | 10.5 | 9 | 0.5 | 38.0947 | 44 | 0.013
39 | TR_4 | 4 | Bog | 2019-02-28 | 11.6 | 11.8973 | 0.5 | 38.9 | 30.28 | 0.005
40 | TR_5 | 5 | Bog | 2006-07-25 | 7.7 | 4 | 5 | 19.5071 | 41.52 | 0.167
41 | TR_5 | 5 | Bog | 2008-04-14 | 11.5 | 5 | 5.5 | 20.4855 | 38.6 | 0.183
42 | TR_5 | 5 | Bog | 2009-01-21 | 11.2 | 7 | 5.5 | 19.3959 | 52.88 | 0.205
43 | TR_5 | 5 | Bog | 2010-12-01 | 10.1 | 7 | 5.5 | 18.9931 | 41.1 | 0.219
44 | TR_5 | 5 | Bog | 2012-03-26 | 13 | 6 | 6 | 18.5092 | 48.4 | 0.243
45 | TR_5 | 5 | Bog | 2013-04-15 | 17.4 | 8 | 6 | 19.0383 | 47.16 | 0.239
46 | TR_5 | 5 | Bog | 2014-02-28 | 17.3 | 7 | 6 | 17.6402 | 43.32 | 0.249
47 | TR_5 | 5 | Bog | 2015-06-05 | 22.9 | 10 | 6 | 19.0194 | 42.44 | 0.317
48 | TR_5 | 5 | Bog | 2017-01-04 | 22.6 | 10 | 6 | 16.5293 | 43.54 | 0.321
49 | TR_5 | 5 | Bog | 2017-08-18 | 16.7 | 12 | 5.5 | 18.2084 | 46.08 | 0.352
50 | TR_5 | 5 | Bog | 2018-02-21 | 20.5 | 10 | 6 | 17.2672 | 44.14 | 0.323
51 | TR_5 | 5 | Bog | 2019-02-20 | 20.1 | 14.1885 | 6 | 11.52 | 34.9 | 0.345
52 | TR_6 | 6 | Bog | 2016-07-21 | 4.5 | 0 | 0.5 | 42.0876 | 42.46 | 0.013
53 | TR_6 | 6 | Bog | 2017-02-21 | 13.9 | 8 | 0.5 | 41.4264 | 34.24 | 0.005
54 | TR_6 | 6 | Bog | 2018-02-21 | 8.9 | 9 | 0.5 | 36.1652 | 37.84 | 0.015
55 | TR_6 | 6 | Bog | 2019-02-28 | 15.2 | 23.2163 | 0.5 | 35.95 | 23.72 | 0.005
56 | TR_7 | 7 | Bog | 2012-03-26 | 3.9 | 3 | 0.5 | 39.698 | 51.88 | 0.004
57 | TR_7 | 7 | Bog | 2013-04-16 | 3.8 | 1 | 0.5 | 40.204 | 52.12 | 0.007
58 | TR_7 | 7 | Bog | 2014-02-24 | 3.7 | 3 | 0.5 | 36.1125 | 46.86 | 0.008
59 | TR_7 | 7 | Bog | 2015-06-04 | 3.2 | 3 | 0.5 | 36.4348 | 55.76 | 0.015
60 | TR_7 | 7 | Bog | 2017-03-23 | 4.3 | 5 | 0.5 | 37.3758 | 22.1 | 0.015
61 | TR_7 | 7 | Bog | 2019-03-27 | 5.8 | 5.7244 | 0.5 | 36.49 | 33.28 | 0.026
62 | TR_8 | 8 | Bog | 2007-02-07 | 7.3 | 5 | 2 | 32.1938 | 47.32 | 0.01
63 | TR_8 | 8 | Bog | 2009-06-26 | 9.1 | 8 | 2 | 28.5858 | 41.78 | 0.034
64 | TR_8 | 8 | Bog | 2010-12-01 | 12.1 | 9 | 2.5 | 26.8833 | 42.96 | 0.032
65 | TR_8 | 8 | Bog | 2012-01-12 | 11.9 | 8 | 2 | 25.2471 | 37.72 | 0.038
66 | TR_8 | 8 | Bog | 2013-04-29 | 12.4 | 8 | 2.5 | 25.6321 | 37.88 | 0.052
67 | TR_8 | 8 | Bog | 2014-02-14 | 11.5 | 8 | 2.5 | 24.6367 | 32.82 | 0.063
68 | TR_8 | 8 | Bog | 2016-05-20 | 15.3 | 12 | 2.5 | 23.2634 | 41.5 | 0.07
69 | TR_8 | 8 | Bog | 2017-02-03 | 12.1 | 10 | 3 | 21.915 | 34.02 | 0.078
70 | TR_8 | 8 | Bog | 2018-02-27 | 8.4 | 5 | 3 | 21.2643 | 19.94 | 0.092
71 | TR_9 | 9 | Bog | 2008-11-24 | 5.3 | 3 | 0.5 | 45.8457 | 35.82 | 0.005
72 | TR_9 | 9 | Bog | 2009-02-24 | 4.5 | 3 | 0.5 | 43.0363 | 40.04 | 0.004
73 | TR_9 | 9 | Bog | 2010-04-13 | 5 | 3 | 0.5 | 43.6962 | 50.98 | 0.005
74 | TR_9 | 9 | Bog | 2011-11-16 | 5.9 | 4 | 0.5 | 40.8912 | 41.14 | 0.009
75 | TR_9 | 9 | Bog | 2013-05-30 | 3.4 | 3 | 0.5 | 44.0785 | 36.54 | 0.007
76 | TR_9 | 9 | Bog | 2014-04-08 | 4.3 | 3 | 0.5 | 43.6789 | 39.18 | 0.008
77 | TR_9 | 9 | Bog | 2016-06-21 | 3.5 | 2 | 1 | 44.1476 | 51.14 | 0.008
78 | TR_9 | 9 | Bog | 2017-04-18 | 4.2 | 3 | 1 | 42.1966 | 36.22 | 0.01
79 | TR_9 | 9 | Bog | 2018-05-15 | 8.75 | 5 | 1.5 | 35.4083 | 32.76 | 0.005
80 | TR_9 | 9 | Bog | 2019-04-03 | 7.4 | 6.5177 | 1.5 | 36.24 | 39.96 | 0.011
81 | TR_10 | 10 | Bog | 2007-03-26 | 16.9 | 17 | 5.5 | 19.2556 | 39.2 | 0.077
82 | TR_10 | 10 | Bog | 2009-01-22 | 11.7 | 10 | 6 | 20.8326 | 42.9 | 0.109
83 | TR_10 | 10 | Bog | 2011-09-21 | 13.5 | 10 | 6 | 19.6038 | 51.06 | 0.111
84 | TR_10 | 10 | Bog | 2013-08-02 | 16 | 9 | 6 | 20.7393 | 48.78 | 0.14
85 | TR_10 | 10 | Bog | 2014-07-15 | 16 | 12 | 7 | 19.8468 | 52.1 | 0.154
86 | TR_10 | 10 | Bog | 2016-07-21 | 17.3 | 7 | 7 | 17.6257 | 54.68 | 0.173
87 | TR_10 | 10 | Bog | 2017-04-27 | 17.4 | 21 | 7 | 19.1555 | 39.56 | 0.162
88 | TR_10 | 10 | Bog | 2019-04-08 | 21.9 | 33.4498 | 7 | 20.46 | 21.56 | 0.096
89 | TR_11 | 11 | Bog | 2007-07-09 | 6.2 | 7 | 2.5 | 27.9352 | 39.76 | 0.038
90 | TR_11 | 11 | Bog | 2008-12-23 | 6.4 | 8 | 2.5 | 26.8616 | 41.84 | 0.044
91 | TR_11 | 11 | Bog | 2009-01-29 | 8.1 | 7 | 3 | 27.0044 | 41.56 | 0.046
92 | TR_11 | 11 | Bog | 2010-02-23 | 10.9 | 6 | 3 | 27.4264 | 52.24 | 0.065
93 | TR_11 | 11 | Bog | 2012-09-24 | 11.4 | 11 | 3 | 27.0257 | 41.44 | 0.053
94 | TR_11 | 11 | Bog | 2014-05-19 | 16.5 | 7 | 3.5 | 24.7095 | 39.74 | 0.077
95 | TR_11 | 11 | Bog | 2015-06-11 | 7.8 | 9 | 3.5 | 23.7503 | 39.56 | 0.092
96 | TR_11 | 11 | Bog | 2016-06-17 | 14 | 15 | 3.5 | 21.5221 | 40.68 | 0.081
97 | TR_11 | 11 | Bog | 2017-02-22 | 12.4 | 5 | 3.5 | 25.3714 | 52.74 | 0.096
98 | TR_11 | 11 | Bog | 2018-11-13 | 16.1 |  | 4 | 21.5 | 42.66 | 0.061
99 | TR_12 | 12 | Bog | 2007-03-28 | 19.5 | 0 | 2 | 30.2317 | 35.86 | 0.047
100 | TR_12 | 12 | Bog | 2009-02-24 | 14.3 | 0 | 2.5 | 27.5958 | 35.08 | 0.057
101 | TR_12 | 12 | Bog | 2010-11-12 | 21.4 | 12 | 2.5 | 27.7551 | 30.56 | 0.061
102 | TR_12 | 12 | Bog | 2011-10-18 | 19 | 23 | 2.5 | 26.68 | 41.58 | 0.059
103 | TR_12 | 12 | Bog | 2012-01-11 | 24.8 | 20 | 2.5 | 27.3164 | 30.76 | 0.064
104 | TR_12 | 12 | Bog | 2013-04-12 | 22.8 | 19 | 2.5 | 27.798 | 36.2 | 0.066
105 | TR_12 | 12 | Bog | 2014-02-06 | 23.1 | 16 | 2.5 | 27.7324 | 40.78 | 0.079
106 | TR_12 | 12 | Bog | 2017-02-17 | 28.5 | 20 | 3 | 22.48 | 18.6 | 0.089
Note on F1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Contenido de agua (mg/kg)
Note on G1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Saturación en %
Note on H1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Color (sin unidades)
Note on I1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tensión interfacial en (mN/m)
Note on J1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rigidez dieléctrica en (kV)
Note on K1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Número ácido en (mg KOH/g)

## FURANS
Test_ID | Pos | Serial | Location | Date | F_5H2F | F_2FOL | F_2FAL | F_2ACF | F_5M2F
1 | TR_1 | 1 | Bog | 2015-04-22 | 0 |  | 20 | 0 | 6
2 | TR_1 | 1 | Bog | 2015-06-17 | 0 |  | 19 | 0 | 0
3 | TR_1 | 1 | Bog | 2015-06-17 | 0 |  | 11 | 0 | 0
4 | TR_1 | 1 | Bog | 2015-12-12 | 0 |  | 5 | 0 | 7
5 | TR_1 | 1 | Bog | 2017-07-13 | 0 |  | 0 | 0 | 0
6 | TR_1 | 1 | Bog | 2018-06-21 | 0 | 0 | 0 | 0 | 0
7 | TR_1 | 1 | Bog | 2019-03-18 | 0 | 91 | 0 | 0 | 0
8 | TR_2 | 2 | Bog | 2012-02-17 | 4 | 609 | 167 | 0 | 0
9 | TR_2 | 2 | Bog | 2013-09-06 | 0 | 0 | 544 | 0 | 0
10 | TR_2 | 2 | Bog | 2014-05-26 | 0 |  | 428 | 0 | 0
11 | TR_2 | 2 | Bog | 2015-06-18 | 0 |  | 590 | 0 | 0
12 | TR_2 | 2 | Bog | 2017-07-17 | 0 |  | 112 | 0 | 0
13 | TR_2 | 2 | Bog | 2019-01-11 | 0 | 260 | 204 | 35 | 0
14 | TR_3 | 3 | Bog | 2011-08-26 | 0 | 0 | 15 | 1 | 2
15 | TR_3 | 3 | Bog | 2013-09-25 | 0 | 0 | 17 | 0 | 0
16 | TR_3 | 3 | Bog | 2014-07-18 | 0 |  | 0 | 0 | 0
17 | TR_3 | 3 | Bog | 2015-04-22 | 0 |  | 110 | 0 | 0
18 | TR_3 | 3 | Bog | 2017-06-27 | 0 |  | 200 | 0 | 0
19 | TR_3 | 3 | Bog | 2019-01-11 | 0 | 1179 | 0 | 0 | 0
20 | TR_3 | 3 | Bog | 2019-02-20 | 161 | 2500 | 1358 | 213 | 0
21 | TR_4 | 4 | Bog | 2012-09-19 | 0 | 0 | 2 | 0 | 0
22 | TR_4 | 4 | Bog | 2014-10-03 | 0 |  | 9 | 0 | 0
23 | TR_4 | 4 | Bog | 2017-06-22 | 0 |  | 10 | 0 | 0
24 | TR_4 | 4 | Bog | 2018-06-20 | 0 | 0 | 0 | 0 | 0
25 | TR_4 | 4 | Bog | 2019-02-28 | 0 | 351 | 0 | 0 | 0
26 | TR_5 | 5 | Bog | 2012-07-25 | 45 | 20 | 1436 | 0 | 0
27 | TR_5 | 5 | Bog | 2013-05-10 | 77 | 76 | 1529 | 0 | 59
28 | TR_5 | 5 | Bog | 2014-04-23 | 60 |  | 590 | 0 | 58
29 | TR_5 | 5 | Bog | 2015-06-17 | 21 |  | 2377 | 0 | 65
30 | TR_5 | 5 | Bog | 2017-02-28 | 169 |  | 3963 | 0 | 0
31 | TR_5 | 5 | Bog | 2017-09-08 | 41 |  | 3428 | 0 | 93
32 | TR_5 | 5 | Bog | 2018-06-05 | 0 | 0 | 2816 | 0 | 0
33 | TR_5 | 5 | Bog | 2019-02-20 | 3634 | 20510 | 11684 | 916 | 539
34 | TR_6 | 6 | Bog | 2017-03-03 | 0 |  | 0 | 0 | 0
35 | TR_6 | 6 | Bog | 2019-01-11 | 0 | 0 | 0 | 0 | 0
36 | TR_6 | 6 | Bog | 2019-02-28 | 0 | 0 | 152 | 0 | 0
37 | TR_7 | 7 | Bog | 2012-07-25 | 0 | 0 | 0 | 0 | 0
38 | TR_7 | 7 | Bog | 2013-05-23 | 0 | 0 | 7 | 6 | 0
39 | TR_7 | 7 | Bog | 2014-04-23 | 0 |  | 0 | 0 | 0
40 | TR_7 | 7 | Bog | 2015-06-17 | 3 |  | 6 | 0 | 0
41 | TR_7 | 7 | Bog | 2017-02-24 | 0 |  | 12 | 0 | 0
42 | TR_7 | 7 | Bog | 2017-06-21 | 0 |  | 0 | 0 | 0
43 | TR_7 | 7 | Bog | 2019-01-12 | 0 | 75 | 0 | 0 | 0
44 | TR_7 | 7 | Bog | 2019-03-27 | 0 | 182 | 94 | 0 | 77
45 | TR_8 | 8 | Bog | 2012-02-17 | 0 | 0 | 23 | 6 | 16
46 | TR_8 | 8 | Bog | 2013-09-04 | 0 | 65 | 62 | 0 | 77
47 | TR_8 | 8 | Bog | 2014-02-18 | 0 |  | 94 | 0 | 0
48 | TR_8 | 8 | Bog | 2017-02-28 | 0 |  | 203 | 0 | 0
49 | TR_8 | 8 | Bog | 2018-06-20 | 0 | 0 | 82 | 0 | 0
50 | TR_9 | 9 | Bog | 2011-11-24 | 0 | 0 | 4 | 7 | 0
51 | TR_9 | 9 | Bog | 2014-05-26 | 0 |  | 0 | 0 | 0
52 | TR_9 | 9 | Bog | 2017-07-07 | 0 |  | 0 | 0 | 0
53 | TR_9 | 9 | Bog | 2018-06-21 | 0 | 0 | 0 | 0 | 0
54 | TR_9 | 9 | Bog | 2019-04-03 | 0 | 202 | 90 | 59 | 0
55 | TR_10 | 10 | Bog | 2011-10-06 | 18 | 0 | 449 | 0 | 10
56 | TR_10 | 10 | Bog | 2013-09-25 | 0 |  | 553 | 0 | 0
57 | TR_10 | 10 | Bog | 2014-07-21 | 21 |  | 644 | 0 | 0
58 | TR_10 | 10 | Bog | 2017-07-13 | 54 |  | 855 | 0 | 0
59 | TR_10 | 10 | Bog | 2019-04-08 | 142 | 5051 | 3730 | 207 | 0
60 | TR_11 | 11 | Bog | 2012-11-15 | 0 | 0 | 0 | 0 | 0
61 | TR_11 | 11 | Bog | 2014-06-27 | 0 |  | 0 | 0 | 0
62 | TR_11 | 11 | Bog | 2015-06-18 | 0 |  | 17 | 0 | 0
63 | TR_11 | 11 | Bog | 2017-03-06 | 0 |  | 95 | 0 | 0
64 | TR_12 | 12 | Bog | 2011-11-01 | 0 | 0 | 503 | 0 | 0
65 | TR_12 | 12 | Bog | 2012-02-17 | 0 | 0 | 148 | 5 | 18
66 | TR_12 | 12 | Bog | 2013-04-19 | 0 | 0 | 540 | 20 | 56
67 | TR_12 | 12 | Bog | 2014-02-11 | 0 |  | 761 | 21 | 53
68 | TR_12 | 12 | Bog | 2017-03-02 | 0 |  | 1852 | 25 | 93

## Electric_Test
Test_ID | Pos | Serial | Location | Date | PF | IP | WR | IR | TR
1 | TR_2 | 2 | TR_2 | 2017-05-10 | 0.1 | 2 | 0.9 | 650 | 0.1
2 | TR_2 | 2 | TR_2 | 2016-07-06 | 0.25 | 1.1 | 1 | 500 | 0.2
3 | TR_2 | 2 | TR_2 | 2015-06-03 | 1.2 | 1.75 | 2 | 450 | 0.3
4 | TR_2 | 2 | TR_2 | 2014-03-31 | 1.5 | 1.5 | 1.25 | 5 | 0.5
5 | TR_2 | 2 | TR_2 | 2013-05-16 | 1.6 | 1.5 | 1.3 | 50 | 0.6
6 | TR_4 | 4 | TR_4 | 2017-01-04 | 0.1 | 2 | 0.9 | 650 | 0.1
7 | TR_4 | 4 | TR_4 | 2014-02-06 | 0.25 | 1.1 | 1 | 500 | 0.2
8 | TR_4 | 4 | TR_4 | 2013-03-21 | 1.2 | 1.75 | 2 | 450 | 0.3
9 | TR_4 | 4 | TR_4 | 2013-03-21 | 1.5 | 1.5 | 1.25 | 5 | 0.5
10 | TR_4 | 4 | TR_4 | 2013-03-08 | 1.6 | 1.5 | 1.3 | 50 | 0.6
Note on F1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Factor de potencia en p.u.
Note on G1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Polarización
Note on H1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Resistencia de los devanados en % de fábrica
Note on I1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Resistencia de aislamiento en MΩ
Note on J1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Relación de transformación en % de error

## OPERATION
Test_ID | Pos | Serial | Location | Date | LF | AT | HS | A | Replacement
1 | TR2 | 39TR2 | TR2 | 2017-05-11 | 0.8 | 24 | 90 | 0 | TRUE
2 | TR2 | 39TR2 | TR2 | 2016-07-06 | 0.9 | 23 | 95 | 0 | TRUE
3 | TR2 | 39TR2 | TR2 | 2015-06-11 | 1 | 24 | 100 | 0 | TRUE
4 | TR2 | 39TR2 | TR2 | 2014-04-21 | 1.1 | 22 | 100 | 0 | TRUE
5 | TR2 | 39TR2 | TR2 | 2013-05-30 | 1 | 23 | 98 | 0 | TRUE
6 | TR4 | 39TR4 | TR4 | 2017-02-16 | 1 | 20 | 100 | 0 | FALSE
7 | TR4 | 39TR4 | TR4 | 2014-02-06 | 1.2 | 21 | 110 | 0 | FALSE
8 | TR4 | 39TR4 | TR4 | 2013-04-09 | 1.2 | 21 | 105 | 0 | FALSE
9 | TR4 | 39TR4 | TR4 | 2013-04-09 | 1.5 | 21 | 105 | 0 | FALSE
10 | TR4 | 39TR4 | TR4 | 2013-04-09 | 1.2 | 23 | 100 | 0 | FALSE

## OLTC_Test
Test_ID | Pos | Serial | Location | Date | NO | YS
1 | TR2 | 39TR2 | TR2 | 2017-05-11 | 230000 | 44
2 | TR2 | 39TR2 | TR2 | 2016-07-06 | 200000 | 43
3 | TR2 | 39TR2 | TR2 | 2015-06-11 | 180000 | 42
4 | TR2 | 39TR2 | TR2 | 2014-04-21 | 160000 | 41
5 | TR2 | 39TR2 | TR2 | 2013-05-30 | 150000 | 40
6 | TR4 | 39TR4 | TR4 | 2017-02-16 | 250000 | 24
7 | TR4 | 39TR4 | TR4 | 2014-02-06 | 200000 | 21
8 | TR4 | 39TR4 | TR4 | 2013-04-09 | 180000 | 20
9 | TR4 | 39TR4 | TR4 | 2013-04-09 | 180000 | 20
10 | TR4 | 39TR4 | TR4 | 2013-04-09 | 180000 | 20

## Bushing_Test
Test_ID | Pos | Serial | Location | Date | PF_B | C
1 | TR2 | 39TR2 | TR2 | 2017-05-11 | 0.7 | 1
2 | TR2 | 39TR2 | TR2 | 2016-07-06 | 0.6 | 0.75
3 | TR2 | 39TR2 | TR2 | 2015-06-11 | 0.6 | 0.7
4 | TR2 | 39TR2 | TR2 | 2014-04-21 | 0.5 | 0.6
5 | TR2 | 39TR2 | TR2 | 2013-05-30 | 0.45 | 0.5
6 | TR4 | 39TR4 | TR4 | 2017-02-16 | 0.7 | 1
7 | TR4 | 39TR4 | TR4 | 2014-02-06 | 0.6 | 0.75
8 | TR4 | 39TR4 | TR4 | 2013-04-09 | 0.6 | 0.7
9 | TR4 | 39TR4 | TR4 | 2013-04-09 | 0.5 | 0.6
10 | TR4 | 39TR4 | TR4 | 2013-04-09 | 0.45 | 0.5

## Criticality_Test
Test_ID | Pos | Serial | Location | Date | ENS (MWh) | MMTR (hrs) | MMTF (hrs) | PCB
1 | TR2 | 39TR2 | TR2 | 2017-05-11 | 12 | 400 | 24 | TRUE
2 | TR4 | 39TR4 | TR4 | 2017-02-16 | 5 | 336 | 15 | TRUE

## _56F9DC9755BA473782653E2940F9 (hidden)
2MF_VyIJjkWHv-xPRV62AFp6FmJGvDJDlaNXvDlwm8NUQVQ5TFVKRllOUTRMWlBJS0syOUhLSFNOVi4u
Form1
{dcbd5c6e-e310-4cb1-a15e-380c47f2a6be}